## Sheet2
General Programme management
Ref. | Question | Comments
1. Programme management
1.1 | Is there a responsible person agreed for every water system nominated in writing?
1.2 | Is there an appointed deputy?
1.3 | Are the duties of all persons involved clearly defined and communicated?
1.4 | Are all persons involved adequately trained?
1.5 | Are the responsibilities of the occupier and contractor(s) clearly defined?
1.6 | Has it been ensured that the contractors are adequately trained and competent?
1.7 | Have the other relevant health and safety issues - COSHH assessments for chemicals, safe access etc. been addressed?
Cooling Towers
1. Physical Condition and design
1.1 | Are the drift eliminators suitable, in good condition and effective?
1.2 | Is the system water in good condition?
1.3 | Is the sump free from sediment?
1.4 | Are all visible surfaces free from slime or algae?
1.5 | Are all visible surfaces free from scale deposits?
1.6 | Are all visible surfaces free from corrosion?
1.7 | Is the water flow even across the whole of the tower fill?
1.8 | Have all the dead legs or poor flow areas been eliminated?
1.9 | Has all redundant plant been isolated from the system?
1.1 | Are all pipe runs as short and direct as possible?
1.11 | Is the tower constructed of impervious materials?
1.12 | If constructed of wood, is this in good condition?
2. Risk Assessment (General)
2.1 | Has the existence of the cooling tower/evaporative condenser been notified to the local authority?
2.2 | Is there a written risk assessment for the system?
2.3 | Does it contain an up to date schematic plan of the system?
2.4 | Does it contain details of the precautions to be taken?
2.5 | Does it contain instructions for the operation of the system?
2.6 | Does the assessment conclude that the risk?
2.7 | Does the assessment consider the tower's physical condition?
2.8 | Does it consider the tower's positioning?
2.9 | Does it consider the population density near the premises?
2.1 | Does it consider any 'at risk' groups of persons?
2.11 | Has elimination or replacement with a lower risk system been properly considered?
3. Schematic Diagram
3.1 | Does it show all system control valves?
3.2 | Does it show standby plant (spare pumps etc)?
3.3 | Does it show any associated storage tanks?
3.4 | Does it show system bleed valve?
3.5 | Does it show chemical dosing pumps and injection points?
3.6 | Does it show system drain valve?
3.7 | Does it show the origin of the water supply?
4. Cleaning and Disinfection
4.1 | Is there a written cleaning and disinfection procedure?
4.2 | Is it carried out at least every six months?
4.3 | Does it specify chlorine level at start of pre-clean chlorination?
4.4 | Does it specify contact/circulation time?
4.5 | Does it specify chlorine level at end of pre-clean chlorination?
4.6 | Does it give the method for cleaning all accessible parts?
4.7 | Does it specify chlorine levels at start of post-clean chlorination?
4.8 | Does it specify contact/circulation time?
4.9 | Does it specify chlorine level at end of post-clean chlorination?
4.1 | Is the removal of the tower fill/pack for cleaning and disinfection specified in the assessment?
4.11 | Are they removed for cleaning and disinfection in practice?
4.12 | Are there suitable health and safety procedures for carrying out cleaning and disinfection?
5. Ongoing Water Treatment
5.1 | Is a water treatment programme in place?
5.2 | Does it use chemicals to control scale?
5.3 | Does it use chemicals to control corrosion?
5.4 | Does it use chemicals to control bacterial and algae (biocides)?
5.5 | Are alternating biocides used?
5.6 | Are the chemicals automatically dosed?
5.7 | Is there an automatic bleed to control dissolved solids?
6. Ongoing Safe Operation
6.1 | Are there procedures for circulation of all parts once per week?
6.2 | Is there a shutdown of the installation at least once per year? How long does it last?
6.3 | Are there procedures for start up after shutdowns?
6.4 | Instructions for draining during long shutdowns?
6.5 | Instructions regarding valve settings for normal operation?
6.6 | Procedures for switching duty/standby pumps.
7. Monitoring and Record Keeping
7.1 | Daily check to ensure conformance with operating procedures?
7.2 | Daily visual check made on the cleanliness of the system water?
7.3 | Chemical water quality checks carried out at least monthly?
7.4 | System physical condition checks carried out at least weekly?
7.5 | Dip slide tests taken at least weekly?
7.6 | Are Legionella tests carried out every quarter?
7.7 | Records of all tests undertaken maintained?
7.8 | Recommendations for remedial action recorded?
7.9 | Completion of remedial action recorded?
Hot and Cold water systems
Ref. | Question | Comments
1. Physical Condition and Design
1.1 | Is the cold water storage tank adequately lagged?
1.2 | Is the cold water storage tank adequately covered, insect screened and reasonably clean?
1.3 | Is the hot water storage tank/calorifier adequately lagged?
1.4 | Are there any materials that do not comply with the water fittings regulations?
1.5 | Does the Cold Water tank hold more than can be used in 24 hours?
1.6 | Is the stored cold water temperature above 20oC?
1.7 | Is the stored hot water temperature below 60oC?
1.8 | Is the cold water temperature at the furthest draw-off point above 20oC?
1.9 | Is the hot water temperature at the furthest draw-off point below 50oC?
1.1 | Are there any dead ends?
1.11 | Are there any little used outlets (for example outhouses etc.)?
1.12 | Are showers fed from storage tanks (as opposed to electric)?
1.13 | Are there systems other than showers that can generate aerosols?
2. Risk assessment
2.1 | Is there a written risk assessment for the system?
2.2 | Does it contain an up to date schematic plan of the system?
2.3 | Does it contain details of the precautions to be taken?
2.4 | Does it contain instructions for the operation of the system?
2.5 | Does the assessment conclude that there is a significant risk?
2.6 | Does the assessment consider the physical condition of tanks, calorifiers and pipework?
2.7 | Has elimination or replacement with a lower risk system been properly considered?
3. Inspection and Maintenance
3.1 | Are the temperatures of hot water calorifiers regularly monitored?
3.2 | Are Cold water tank temperatures regularly monitored?
3.3 | Are tap outlet temperatures regularly monitored?
3.4 | Is the physical condition of Calorifiers and Water tanks regularly checked, cleaned and disinfected as necessary?
3.5 | Are Shower heads regularly de-scaled?
3.6 | Are little used outlets flushed through regularly?